## SelectionData
Selection Table
flow rate, Q | [m³/h] | 1200
diffuser length, L | [mm] | 1000 | 150 mm £ L £ 2000 mm
diffuser height, H | [mm] | 300 | 100 mm £ H £ 600 mm
throw, LT | [m] | 6 | with ceiling effect
supply temperature, Ts | [°C] | 15
room temperature, Tr | [°C] | 20
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | B-600 | B-600 | B-600 | B-600 | B-600
| L [mm] | 1000 | 1000 | 1000 | 1000 | 1000
| H [mm] | 200 | 250 | 300 | 350 | 400
| Damper | GT007 | GT007 | GT007 | GT007 | GT007
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
effective air velocity, Veff | [m/s] | 3.3724 | 2.6367 | 2.1645 | 1.8357 | 1.5937
total pressure, DPtot | [Pa] | 5.6865 | 3.4761 | 2.3425 | 1.685 | 1.2699
throw velocity, vT @ LT | [m/s] | 0.51644 | 0.45665 | 0.41374 | 0.38103 | 0.35502
critical distance | [m] | - | - | - | - | -
air temperature @ LT | [°C] | 18.3866 | 18.1753 | 17.9861 | 17.8132 | 17.653
sound power, Lw | [dB(A)] | 36.7783 | 32.4391 | 28.8354 | 25.7235 | 22.9637
sound pressure, Lp | [dB(A)] | 28.7783 | 24.4391 | 20.8354 | <20 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | - | - | - | - | -
250 | [Hz] | - | - | - | - | -
500 | [Hz] | - | - | - | - | -
1000 | [Hz] | - | - | - | - | -
2000 | [Hz] | - | - | - | - | -
4000 | [Hz] | - | - | - | - | -
8000 | [Hz] | - | - | - | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | A600 | A600 | A600 | A600 | A600
|  | Size | 200 | 250 | 300 | 350 | 400
|  | condition 1 | 1000 mm | 1000 mm | 1000 mm | 1000 mm | 1000 mm
|  | condition 2 | GT007 | GT007 | GT007 | GT007 | GT007
|  | condition 3 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
THROW
|  | Ak [m²] | 0.098842 | 0.12642 | 0.154 | 0.18158 | 0.20916
|  | K1 [m] | 2.9226 | 2.9226 | 2.9226 | 2.9226 | 2.9226
|  | X0 [m] | 0 | 0 | 0 | 0 | 0
PRESSURE LOSS
|  | A | 503.2218 | 643.6309 | 784.04 | 924.4491 | 1064.8581
|  | B | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
total pressure loss |  | Aduct [m²]
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
|  | Ak [m²] | 0.098842 | 0.12642 | 0.154 | 0.18158 | 0.20916
|  | K2 [-] | 6.081 | 6.081 | 6.081 | 6.081 | 6.081
|  | X0 [m] | 0.075261 | 0.075261 | 0.075261 | 0.075261 | 0.075261
SOUND POWER, NR
|  | A | 20.2665 | 20.1781 | 20.0897 | 20.0013 | 19.9129
|  | B | -111.9128 | -115.6252 | -118.6021 | -121.0873 | -123.2203
SOUND POWER, dB(A)
|  | A | 20.2665 | 20.1781 | 20.0897 | 20.0013 | 19.9129
|  | B | -106.9128 | -110.6252 | -113.6021 | -116.0873 | -118.2203
SOUND POWER SPECTRUM
| at 125 Hz | A
B
| at 250 Hz | A
B
| at 500 Hz | A
B
| at 1 kHz | A
B
| at 2 kHz | A
B
| at 4 kHz | A
B
| at 8 kHz | A
B
END
angle air supply [°] |  |  | 0 | 0 | 0 | 0 | 0
K1 multiplicative correction factor - no Coanda [-] |  |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
correction for angle deflection lamellae
| 15° | Ak [multiplication]
K1 [multiplication]
K2 [multiplication]
Lw [addition]

## IntermediateCalcul (hidden)
Critical distance
Type | A600 | A600 | A600 | A600 | A600
Size | 200 | 250 | 300 | 350 | 400
condition 1 | 1000 mm | 1000 mm | 1000 mm | 1000 mm | 1000 mm
condition 2 | GT007 | GT007 | GT007 | GT007 | GT007
condition 3 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
5
dT1
dT2
A1
A2
B1
B2
L | H
150 | 100
175 | 125
200 | 150
225 | 175
250 | 200
275 | 225
300 | 250
325 | 275
350 | 300
375 | 325
400 | 350
425 | 375
450 | 400
475 | 425
500 | 450
525 | 475
550 | 500
575 | 525
600 | 550
625 | 575
650 | 600
675
700
725
750
775
800
825
850
875
900
925
950
975
1000
1025
1050
1075
1100
1125
1150
1175
1200
1225
1250
1275
1300
1325
1350
1375
1400
1425
1450
1475
1500
1525
1550
1575
1600
1625
1650
1675
1700
1725
1750
1775
1800
1825
1850
1875
1900
1925
1950
1975
2000

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | -3.0985e-05
Throw correction - diffuser length
cK1 | 1