## SelectionData
Selection Table
flow rate, Q | [m³/h] | 400
throw, LT | [m] | 3
supply temperature, Ts | [°C] | 16
room temperature, Tr | [°C] | 26
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | WS400S | WS400S | WS400S | WS400S | WS400S
| Nominal Size | 125 | 160 | 200 | 250 | 315
| Plenum | WP100S | WP100S | WP100S | WP100S | WP100S
| Ø Spigot | 125 | 160 | 200 | 250 | 315
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
duct air velocity, Vduct | [m/s] | 9.0541 | 5.5262 | 3.5368 | 2.2635 | 1.4258
effective air velocity, Veff | [m/s] | 10.101 | 3.9683 | 3.9683 | 1.9841 | 1.9841
static pressure, DPs | [Pa] | 100.379 | 28.3097 | 18.0387 | 6.2761 | 4.1519
total pressure, DPtot | [Pa] | 149.5655 | 46.6331 | 25.544 | 9.3502 | 5.3715
throw velocity, vT @ LT | [m/s] | 0.38285 | 0.2569 | 0.2569 | 0.17963 | 0.17963
critical distance | [m] | - | - | - | - | -
air temperature @ LT | [°C] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
sound power, Lw | [dB(A)] | >55 | 46.387 | 39.1043 | 26.5377 | 20.1354
sound pressure, Lp | [dB(A)] | 53.9085 | 38.387 | 31.1043 | <20 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | 58.094 | 47.5337 | 37.7274 | 37.7274 | 34.0119
250 | [Hz] | 59.2365 | 42.5123 | 31.8062 | 31.8062 | 25.4539
500 | [Hz] | 61.5065 | 36.6776 | 20.5356 | 20.5356 | 14.0358
1000 | [Hz] | 68.0158 | 31.191 | 10.2961 | 10.2961 | 2.4762
2000 | [Hz] | 65.0854 | 20.741 | < BGL | < BGL | < BGL
4000 | [Hz] | 56.0178 | 11.7161 | < BGL | < BGL | < BGL
8000 | [Hz] | < BGL | < BGL | < BGL | < BGL | < BGL
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | WS400S | WS400S | WS400S | WS400S | WS400S
|  | Size | 125 | 160 | 200 | 250 | 315
|  | Plenum | WP100S | WP100S | WP100S | WP100S | WP100S
|  | Ø Spigot | 125 | 160 | 200 | 250 | 315
|  | Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
THROW
|  | Ak [m²] | 0.011 | 0.028 | 0.028 | 0.056 | 0.056
|  | K1 [m] | 1.0842 | 1.1607 | 1.1607 | 1.1477 | 1.1477
|  | X0 [m] | 0 | 0 | 0 | 0 | 0
PRESSURE LOSS
|  | A | 39.9655 | 72.1507 | 101.2284 | 167.8975 | 211.2354
|  | B | 0.49978 | 0.5123 | 0.47505 | 0.47264 | 0.44852
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.049087 | 0.077931
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 29.7301 | 29.3632 | 28.3133 | 27.3963 | 31.7781
|  | B | -120.213 | -134.2024 | -135.9906 | -142.7995 | -177.0768
SOUND POWER, dB(A)
|  | A | 29.1469 | 29.0976 | 28.3602 | 27.3985 | 29.105
|  | B | -112.7242 | -127.9499 | -130.8145 | -137.6193 | -154.2464
SOUND POWER SPECTRUM
| at 125 Hz | A | 20.6165 | 20.0459 | 21.2305 | 18.8399 | 19.6613
|  | B | -65.4289 | -74.2637 | -79.6683 | -75.1513 | -83.7883
| at 250 Hz | A | 22.5018 | 21.6995 | 24.6148 | 23.5602 | 23.795
|  | B | -75.5822 | -83.5402 | -104.9667 | -109.3539 | -117.1128
| at 500 Hz | A | 31.408 | 31.8449 | 36.4274 | 35.7198 | 36.7521
|  | B | -126.6732 | -144.8159 | -181.5759 | -193.4783 | -206.1631
| at 1 kHz | A | 42.6919 | 40.8717 | 44.8515 | 46.0981 | 45.6044
|  | B | -187.7714 | -200.728 | -237.5352 | -265.8988 | -270.7609
| at 2 kHz | A | 51.9953 | 49.1414 | 52.1162 | 54.6174 | 50.1318
|  | B | -246.4424 | -257.4273 | -291.5113 | -331.3769 | -311.0498
| at 4 kHz | A | 56.8519 | 64.225 | 48.2067 | 56.9164 | 48.3694
|  | B | -284.6083 | -358.7931 | -277.1128 | -357.2825 | -308.2437
| at 8 kHz | A
B
END

## IntermediateCalcul (hidden)
Critical distance
Type | WS400S | WS400S | WS400S | WS400S
Size | 125 | 200 | 250 | 315
Plenum | WP100S | WP100S | WP100S | WP100S
Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open)
Ø Spigot | 125 | 200 | 250 | 315
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
10
dT1
dT2
A1
A2
B1
B2